## Load Schedule
Board | Description | Connected kW | Diversity | Demand kW
DB-1 | Lobby lighting + downlights | 4.2 | 0.9 | 3.78
DB-1 | Lobby small power / sockets | 6 | 0.4 | 2.4
DB-2 | Main hall highbay lighting | 9 | 0.9 | 8.1
DB-2 | Stage / AV dedicated outlets | 24 | 0.5 | 12
DB-2 | Hall floor boxes & sockets | 12 | 0.4 | 4.8
DB-3 | Catering / pantry 3-phase outlets | 30 | 0.5 | 15
DB-3 | Washroom & back-of-house power | 8 | 0.4 | 3.2
DB-3 | Hand dryers / water heaters | 12 | 0.5 | 6
DB-4 | Facade lighting feeders (allowance) | 12 | 0.8 | 9.6
DB-4 | External / perimeter services | 5 | 0.7 | 3.5
EM | Emergency & exit lighting (charging) | 0.3 | 1 | 0.3
SEC | CCTV, PoE switches, NVR rack | 3.5 | 1 | 3.5
HVAC | HVAC allowance (by HVAC package) | 120 | 0.75 | 90
| TOTAL | 246 |  | 162.18
| Building only (excl. HVAC) | 126 |  | 72.18
| Apparent power @ pf 0.90 (kVA) |  |  | 180.2

## Boards
Ref | Location / Duty | Specification
MDB | Main Distribution Board | 400/230V TPN, 800A, form 3b, Icu 36kA, SPD T2, MCCB outgoers
DB-1 | Lobby & Front of House | TPN 12-way, 100A MCCB feed, 30mA RCBO finals
DB-2 | Main Hall & Stage | TPN 24-way, 250A MCCB feed, 30mA RCBO finals
DB-3 | Catering & Back of House | TPN 18-way, 160A MCCB feed, 30mA RCBO finals
DB-4 | Facade & External | TPN 8-way, 63A MCCB feed, IP65 enclosure, timeclock
EM-DB | Emergency Lighting Sub-Circuit | SPN 6-way, fed ahead of local isolation
SEC-DB | Security / CCTV Rack Board | SPN 6-way, dedicated clean earth

## Equipment Qty
Item | Description | Unit | Qty
L1 | LED highbay 150W 4000K IP65 | no | 60
L2 | 2x2 recessed LED panel 36W | no | 12
L3 | LED downlight 12W 3000K | no | 24
P1 | 13A twin switched socket outlet | no | 34
P2 | Recessed floor service box | no | 18
EM1 | Maintained LED exit sign, 3hr | no | 7
EM2 | Emergency bulkhead, 3hr | no | 33
SEC1 | IP dome camera 4MP PoE | no | 15
SEC2 | IP bullet camera 4MP IP66 | no | 5
FAC1 | Facade feeder allowance (12 kW, 3 zones) | lot | 1

## Scope
Status | Item
INCLUDED | Main LV panel (MDB) downstream of utility metering
INCLUDED | Sub-distribution boards DB-1..DB-4, EM-DB, SEC-DB
INCLUDED | Internal lighting, switching and final circuits
INCLUDED | Small power, sockets and floor service boxes
INCLUDED | Emergency and exit lighting (3hr integral battery)
INCLUDED | CCTV cameras, PoE switches, NVR, cabling, containment
INCLUDED | Facade lighting feeders, containment and DB-4
INCLUDED | Earthing and bonding within building envelope
EXCLUDED | HT/LT transformer, RMU, substation civil works
EXCLUDED | DISCO/LESCO metering, connection and tariff fees
EXCLUDED | Standby diesel generator, ATS, fuel and acoustics
EXCLUDED | UPS, solar PV and battery energy storage
EXCLUDED | External site and street lighting beyond building line
EXCLUDED | Facade luminaires and specialist lighting design
EXCLUDED | Fire alarm, PA/VA, structured data, BMS
EXCLUDED | HVAC power beyond the MDB outgoing way
EXCLUDED | Civil trenching, ducting and builders work